[image: image1.jpg]£ GasBoy





Gasboy TopKAT PLUS Bid Specification

1.0 General Requirements

System manufacturer must have a minimum of ten (10) years’ experience in the design and manufacture of fuel management equipment. 

The proposed system must conform to ISO 9001:2000 standards for quality management systems.  System shall be UL and cUL approved.

The system must be expandable for future expansions in the number of: fuel sites, vehicles, and drivers.

System shall be Gasboy TopKAT PLUS system or approved equal

2.0 Fueling Procedure

The system shall allow manual fueling.

In manual fueling, a contactless Mifare tag or Mifare card and/or Magnetic stripe card and a keypad for manual entry shall be available as alternative methods for initiating a fueling transaction.

A two stage authorization process shall be provided by identifying both the vehicle and the driver prior to refueling. Both driver and vehicles IDs should be stored in the transaction. The two stage authorization process should be flexible enough to link the vehicle device either to a specific driver or to a list of drivers.

3.0 System Description

3.1 System Configuration

The site controller shall be a stand-alone unit comprising all required peripherals including the central processing unit, display panel, two hose mechanical or eight hose electronic pump control module, communication modules, and optional Receipt Printer.

The site controller shall be web enabled to allow independent real-time control, monitoring and reporting via the web using user ID with password and SSL protected link (https://).

The site controller shall communicate with a central high performance server or dedicated host PC computer for the purpose of centralized control and monitoring of multiple sites. 

Refueling shall take place regardless of the connectivity to the host computer. Refueling limits and restrictions shall be 'pushed' from the host computer to all fuel site controllers enabling off-line refueling with limits and restrictions also when communication is not available. A time limit should be provided for off-line activity to block possible 'break' of the limits by refueling in several sites through the off-line mode.

4.0 Site Controller – TopKAT PLUS
4.1 General

The site controller shall control up to 2 mechanical hoses or, if programmed, 8 electronic Gasboy 9800 Series hoses in one terminal.  

The site controller shall store up to 25,000 transactions and 50,000 vehicles/devices with the ability to set limitations and restrictions.

The site controller shall be available for refueling 24/7.

Site controller shall work in online and off-line modes, in case of communication failures with the FHO software.  When communication is established again, the system shall synchronize data automatically.

The site controller shall have an embedded hardware platform designed to survive the harsh unattended fueling environment. 

The site controller shall use a solid state Flash disk and RTC (Real Time Clock) with back up, along with surge suppressors for transient and noise immunity.  

The system shall include a power fail recovery mechanism.

The CPU shall have no edge connectors and no hard disk (no moving parts)

The site controller shall have a high level data protection through two separate isolated TCP/IP Ethernet network ports. One port shall be used for site peripherals interface and the second port for external communication to the network (Remote access, host computer and 3rd party systems) protected by SSL security. The outside link could use a local modem connection through PPP protocol for TCP/IP communication, cellular, or dial-in type modems.

The site controller shall have the following additional capabilities:

· Secured remote capabilities for monitoring, management and maintenance activities

· Flexible with all types of communication including TCP/IP, wireless Ethernet bridge modems, satellite communications, and dial-up analog modem.

· Web enabled reporting and alarms for Tank Level Sensing (TLS) systems (Veeder Root-350 and VR-450 protocols).  TCP/IP interface to TLS only.  

· Fuel management software for reconciliation reports

· Accessible via Internet browser to control and monitor the system. No requirement to install dedicated software.

· Real time web-based dynamic graphical monitoring and control of dispensers

· Remotely open a pump and limit the quantity to a specific transaction

· Able to update fuel price at a specific time 

· Remote maintenance, remote troubleshoot and remote software upgrades of the various components of the system

The following physical, electrical and environmental specifications shall be provided: 

· Supply voltage: 110– 240 VAC

· Power consumption: 2A max.

· Operating temperature:  -30 C to +70 C

· Communication interface: RS-485–9600 bps, Half-Duplex, RS-232, Ethernet RJ-45-10 Mbps, EIA 802.15.4 

4.2 Tank Level Sensing (TLS) Interface 

The site controller shall support Veeder Root TLS 350 and Veeder Root TLS 450 protocols

The TLS will be connected to the site controller via TCP/IP communication port only to allow fuel management capabilities.  RS 232 interface will not be supported 

The site controller shall have the possibility to define the following communication parameters; Baud rate, Parity, Data bit, Stop bit, Flow control

The site controller shall collect the following data from TLS equipment: 

· 12:00 midnight shift inventory volume for tanks 

· Tank inventory level ; CSLD (Leak Detection) status – Pass/Fail

· Fuel delivery information; Water Level 

· Water levels, Temperature, Alarms (Leak, Overfill, Sump, Sensor, etc)

· Alarms shall flash continuously on the main screen and could be sent via email

4.3 The Pedestal and Dispenser/Pump mount for the TopKAT PLUS
The pedestal shall be a slim (9.5”x9.5”x61”) powder coated metal designed for easy installation and service. The paint application for the entire pedestal terminal shall consist of a positive/negative charged ionization process for superior bonding. All materials shall be tested to sustain Oil, Fuel, Sun, Water and Salt.

The hardware configuration options for the TopKAT PLUS shall be as follows:

1) 9800 Electronic Series Gasboy dispenser/pump mounted TopKAT PLUS
2) 9800 Electronic Series Gasboy pedestal mounted TopKAT PLUS
3) 9800 Electronic Series Gasboy dispenser/pump mounted TopKAT Plus with Receipt Printer

4) 9800 Series Electronic Series Gasboy pedestal mounted TopKAT PLUS with Receipt Printer

5) Mechanical (2-hose control only) Pedestal mounted TopKAT PLUS
6) Mechanical (2-hose control only) Pedestal mounted TopKAT PLUS with Receipt Printer

An Electronic dispenser/pump from other Manufacturers other than Gasboy can only be interfaced to the TopKAT PLUS with a pulse output interface and shall be programmed as mechanical hose outlets (2-hose control only)

The pedestal display panel shall consist of:

· Top illumination utilizing an array of high intensity blue LED’s

· 5” wide x 1.6” high display window

· 4 lines, 20 characters (1/4” height) each, or optional graphic LCD

· LCD operates well in all lightening conditions

· 16 functional keys. The keys shall be rugged and made of metal for higher reliability and longer life (flexible plastic key caps will not be acceptable). 

· The key’s sensors shall use piezoelectric technology for highest reliability

· Magnetic Card Reader

· Mifare Card/Tag Reader

4.4 Receipt Printer (optional)

Optional outdoor receipt printer with 500 ft. paper roll including automatic paper cutter and alarms indicating low-paper and paper-out (alarms shall be available via email and displayed online with secured access).  Receipt Printer door shall be able to be opened with a Manager’s Mifare tag for paper change and test transactions. 

4.5 Site Controller Software 

The system shall be based on web server technology and enable easy secured (SSL) remote access through the network using a standard PC with an internet browser, without the need for any other software application. 

The browser interface shall allow control and monitoring, maintenance activities, report generation with advanced filters and templates, graphical monitoring of fuel levels, on-line pump monitoring and more.

The system shall provide flexibility when searching for data within the system without the need for prior knowledge in SQL or other query languages.

The site controller shall support mechanical and electronic dispensers. All links shall be protected and isolated for maximum reliability.

The system shall store transaction data as well as driver and vehicle records into its database using FLASH disk. Other critical data such as fueling limits and restrictions shall also be stored in the database. 

The system shall use the following authorization devices:

· Mifare cards or tags

· Magnetic Cards (ABA track 2 and 3)

· Keyboard entry authorization
· Two stage authorization using a combination of Mifare/Mag card/Keypad

Authorization schemes shall include the following scenarios:

· Single device authorization

· Two stage authorization (based on two authorization devices)

· Add-on keyboard entries: PIN code, vehicle ID, odometer reading, engine hours

The system shall have the option to collect data from driver before refueling, such as: PIN, Odometer, vehicle ID, etc.

The system shall provide odometer reasonability checks

The site controller shall allow the possibility to work offline with all limits and restrictions


System shall have the option to approve or decline refueling according to pre-defined limits and restrictions for the specific unit.   Such limitations shall include:

· Limit of daily, weekly and monthly refueling volume or sales amount.

· Enable or disable vehicle refueling on specific days (weekdays for example) and/or specific time slots within a day (night time for example)

· Limit the maximum refueling sessions for a specific vehicle per day, week or month.

· Block specific stations for a specific vehicle (if vehicle is restricted for operation in a specific zone).

· Restriction of specific fuel types for refueling of a specific vehicle.

5.0 Host Software

5.1 General

The software shall support multiple fuel site controllers and allow data consolidation.

The software shall support multiple fleets and multiple departments.

The software shall synchronize data with all sites. 

The software shall be used as a centralized issuing and programming facility for Magnetic cards, Mifare cards, and Mifare tags.

The software shall be installed on the host computer running Windows operating system and SQL database that supports ODBC connectivity. 

The system shall be a centralized web server communicating with all sites to provide centralized data base and on-line network access for fleet managers, key personnel and remote maintenance entities. 

The software shall communicate with all sites to provide 24/7 on-line access through the network.

The software shall create and control several fleets and departments and support different privilege levels for limited access for different users (for example, a specific Fleet manager shall only be able to manage only his fleet vehicles). 

The software shall provide advanced on-line services for multiple sites and multiple fleets in a region.

The host software web interface shall use SSL security. 

The software shall provide secure log-in through the Web for each fleet manager, for monitoring & control and report generation including exception reports.

The host software application can interface to other applications via Web Services, import and export of files to FTP and ODBC standard.  

The software shall allow Exporting data to different file formats (using a dropdown menu) such as CSV, TXT, and XML.

The user interface for all software components shall be a web browser.

Mifare tags, Mifare cards and Magnetic cards shall be defined and associated with unique numbers to the fleet vehicles.

6.0 Limits and Restrictions

Host software shall allow limits and restrictions to be configured either by an authorized user or imported from a different external system (using the import/export).

The rules shall be transferred to every site controller to enable off-line activity in case of communication failure; hence a fuel site will be able to refuel a vehicle within its set of limits and restrictions, when communication is down. 

The limits shall be ‘pushed’ into the site controller at a predefined time or for a predefined period of time. Site controllers can also use the limits in an off-line mode (in case of communication failure).

There shall be a graceful period of time (parametric) for this off-line mode since the vehicle could refuel also in other sites (above its limits) while the sites are disconnected from the host computer.  

Customizable vehicle and driver limits and restrictions shall include: 

· Limit of daily, weekly and monthly refueling volume in gallons as well as in currency.

· Enable or disable vehicle refueling on specific days (weekdays for example) and / or specific time slots within a day (night time for example)

· Limit the maximum refueling sessions for a specific vehicle per transaction, per day, week or month.

· Limit the maximum refueling sessions for a specific vehicle per transaction, per day, week or month.

· Block specific stations for a specific vehicle (if vehicle is restricted for operation in a specific zone).

· Block specific stations for a specific vehicle (if vehicle is restricted for operation in a specific zone).

· Restriction of specific fuel types for refueling of a specific vehicle

7.0 Fuel Management System Software

  The host computer shall collect the transactions and TLS information from all fuel sites for centralized fuel management activities including required deliveries, forecasting, reconciliation and more for optimal usage of fuel.

The system shall provide the following capabilities:

· Reports regarding fuel consumption with filters of sites, dates, volumes and more

· Customized templates for specific reports

· History of fuel consumption from every product with graphical representation

· Forecasting consumption for every product based on the consumption history with graphical representation 

· Reconciliation

· Manual entry or editing of fueling transactions

· Provide unified view of ALL stations with regards to fuel level status

· Provide consolidated view of each specific fuel tank, per station

· Provide a centralized system for maintenance reporting and reporting of different system alarms, per station

· Provide an interface for managing of manual stations (without Fuel Controllers)

Tanks status screen from TLS system per site with graphical representation of the tanks 

Alarms (High/Low tanks level, Leak detection, No communication, Etc.)

Export capabilities to other systems (ERP)

8.0 Reporting System

Consolidate data from multiple stations and generate reports, including exception reports, reconciliation reports, trends, forecast, consumption, tank capacity and more. There shall be two types of Reports:

· Custom Reports

· Fuel Management System Reports (built-in)

Custom Reports

The software shall provide a highly flexible custom reporting utility. Data elements can be selected and put in any order by the user to create their own custom report.

This report shall have the ability to be saved as a template for later use.

Must have advanced customized reporting capabilities with filters and templates (Web based).

The custom reports feature shall enable report generation of transactions performed in the fuel station in various profiles.

The following field names shall be used to generate custom reports tables:

Station, Date, Time, Fleet, Transaction Type, Vehicle #, Product, Quantity, Total Sale, Receipt No., Fleet Code, Pay Mode, Transaction Id, Authorized By, Department, PPV, Odometer, Engine Hour, Pump, Tank, Nozzle, Density, Temperature, Vehicle Type, Ref/Slip No., Driver name, Dept. code, Card number, Device name.

The custom report shall allow summary by the following fields (Break by):

Date, Plate, Pump, Product, Pay Mode, Station name, Fleet code, Authorized by, driver name, Dept. code, or a selection of any of the above fields

The custom reports shall allow sorting by the following fields (Sort by):

Date & Time (Ascending/Descending), Pump, Transaction ID, Product, Amount (Ascending/Descending), Quantity, Plate, Pay mode, Station name, fleet code, Receipt ID, Driver name, Dept. code or a selection of any of the above fields.

The above powerful capabilities shall allow flexible reporting such as:

Summary Report – summarizing all transactions of a specific fleet of vehicles.

Vehicle Report – offering the Fleet Manager a detailed transaction report of vehicles pertaining to his fleet, in three cross sections:  

Transactions - providing information regarding each transaction, including the vehicles license plate number, odometer reading, engine hours, fuel type, fuel volume and the transaction ID.

Consumption - listing information regarding each vehicle (device) providing a summation of data (volume consumption, fuel cost, other costs) for each vehicle in a specified time frame.

Exception Reports

The software shall provide Exception Reports for the Fleet Manager. It must provide the ability to spot any abnormal incidents that occurred within his fleet.  The following exception reports are required for each fleet:

Volume Exception Report – shall list noted exceptions relating to the fuel volume consumed in the transactions compared with the related vehicle’s fuel tank volume.   

Mileage Exception Report – shall list the exceptions related to the elapsed distance of the vehicles, according to odometer readings. 

Consumption Exception Report – shall list the exceptions related to the fuel consumption of the vehicles, according to odometer readings and the specified fuel consumption ratio of the vehicle.  

Mileage Exception Report – shall list the exceptions related to the elapsed distance of the vehicles, according to odometer readings. 

Consumption Exception Report – shall list the exceptions related to the fuel consumption of the vehicles, according to odometer readings and the specified fuel consumption ratio of the vehicle.  

Mileage Exception Report – shall list the exceptions related to the elapsed distance of the vehicles, according to odometer readings. 

Consumption Exception Report – shall list the exceptions related to the fuel consumption of the vehicles, according to odometer readings and the specified fuel consumption ratio of the vehicle.  

Not Used Exception Report – shall list the vehicles which did not carry out any transaction in a specified time frame.  The report should include the license plate number, the odometer reading and the date and time of the last transaction performed by the vehicle.

b) Fuel Management System Reports (Built-in)
	Sales

Sales by Tanks Report 

Local Account Transactions

Pump-wise Delivery Report 

Product-wise Dispenser Delivery

Fuel Sales Trends Graph

Fuel Volume Forecast Report 


	Stock Data Reports 
Tanks by Sites

Tanks Trends Graph 

Total Wet Stock Report

Maintenance Reports

Exception Log Reports

Alarm Duration Reports


	Reconciliation Report

Shift Report

Environmental Report

Tank Reconciliation Trends




9.0 Back-up

The system shall provide several back-up mechanisms for maximal data protection as follows:

The database is transmitted periodically to a remote server. The backup can be for the entire database or differential.

Built-in data base back-up mechanism (Customer FTP).

All transactions are exported to a Customer FTP site through an Export Module.

RAID mechanism at the host computer

10.0 Warranty
· 12 month system Parts and Labor warranty 
· 5 year warranty for the Mifare Tags
SP-7186 | 0812​ | 7300 W. Friendly Ave., Greensboro, NC 27410 (336) 547-5700 | www.gasboy.com


[image: image1.jpg]